## Input
0 | Physical Data | [21 empty] | Data for Graphing State Point Analysis | [9 empty] | Click on | above for calculations
| Parameter | Units | Value |  |  |  |  | Model Units | Model Value #1 | Model Value #2 | Settling velocity parameters used to determine gravity flux curve
| Clarifier Diameter | ft | 95 |  | 95 |  |  | m2 | 658.8543 | 658.8543 | Based upon Daigger Equation (1995) |  |  | STP No. 6 Nomenclature | [8 empty] | Solids Concentration |  | Gravity Flux #1 | Gravity Flux #2 | Overflow Rate #1 | Overflow Rate #2 | Underflow Rate #1 | Underflow Rate #2 | Thickening Overloaded?
| Aerated Volume per Clarifier Cluster | MG | 1 |  | 1 |  |  | m3 | 3788.5836 | 3788.5836 | ln V_s = ln V_0 - (k_1 + k_2*SVI)*MLSS | [11 empty] | kg/m3 | mg/L | lbs/sf-d | lbs/sf-d | lbs/sf-d | lbs/sf-d | lbs/sf-d | lbs/sf-d | #1 | #2
[11 empty] | V_s = V_0*exp[-(K_1 + k_2*SVI)*MLSS] | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 31.3271 | 22.7121 | 0 | 0
1 | Data Entry | [9 empty] | ln V_0 | 1.871 | m/h | ln α | [8 empty] | 0.25 | 250 | 7.3502 | 7.3502 | 0.97897 | 0.97897 | 30.3481 | 21.7332 | 0 | 0
| Parameter | Units | Value |  | Value after Adjustment |  |  | Model Units | Model Value #1 | Model Value #2 | k1 | 0.1646 | L/g | γ | [8 empty] | 0.5 | 500 | 13.5594 | 13.5594 | 1.9579 | 1.9579 | 29.3692 | 20.7542 | 0 | 0
| Number of Clarifiers Online in Cluster | [-] | 3 |  | 3 | [5 empty] | k2 | 0.001586 | L/mL | δ | [8 empty] | 0.75 | 750 | 18.7603 | 18.7603 | 2.9369 | 2.9369 | 28.3902 | 19.7752 | 0 | 0
| Influent Flow to Cluster | MGD | 10 |  | 10 | [5 empty] | β | 0 | [10 empty] | 1 | 1000 | 23.0721 | 23.0721 | 3.9159 | 3.9159 | 27.4112 | 18.7963 | 0 | 0
| Flow per Clarifier | MGD | 3.3333 |  | 3.3333 |  |  | m3/h | 525.6944 | 525.6944 | Based upon Ozinsky and Ekama Equation (1995) | [11 empty] | 1.25 | 1250 | 26.6015 | 26.6015 | 4.8949 | 4.8949 | 26.4322 | 17.8173 | 0 | 0
[11 empty] | ln V_s = ln V_0 - β*SVI - ϒ*MLSS - δ*SVI*MLSS | [11 empty] | 1.5 | 1500 | 29.444 | 29.444 | 5.8738 | 5.8738 | 25.4533 | 16.8383 | 0 | 0
| MLSS Concentration | mg/L | 4000 | (Measured) | 2900 | (Anticipated) | See Section 5 to estimate MLSS after an SRT or wasting rate change | kg/m3 | 4 | 2.9 | V_s = V_0*exp[-β*SVI - ϒ*MLSS - δ*SVI*MLSS] | [11 empty] | 1.75 | 1750 | 31.6849 | 31.6849 | 6.8528 | 6.8528 | 24.4743 | 15.8593 | 0 | 0
| RAS Flow per Clarifier | MGD | 3.3333 |  | 3.3333 |  |  | m3/h | 525.6944 | 525.6944 | ln α | 2.1437 | m/h | [9 empty] | 2 | 2000 | 33.4005 | 33.4005 | 7.8318 | 7.8318 | 23.4953 | 14.8804 | 0 | 0
| SVI | mL/g | 100 | (Measured) | 100 | (Anticipated) |  | mL/g | 100 | 100 | γ | 0.20036 | L/g | [9 empty] | 2.25 | 2250 | 34.6589 | 34.6589 | 8.8107 | 8.8107 | 22.5164 | 13.9014 | 0 | 0
| Settleability Curve Used |  | Daigger (SVI) |  | Daigger (SVI) | [5 empty] | δ | 0.00091 | L/mL | [9 empty] | 2.5 | 2500 | 35.5207 | 35.5207 | 9.7897 | 9.7897 | 21.5374 | 12.9224 | 0 | 0
[11 empty] | β | 0.00165 | g/mL | [9 empty] | 2.75 | 2750 | 36.0398 | 36.0398 | 10.7687 | 10.7687 | 20.5584 | 11.9435 | 0 | 0
2 | Data Output | [9 empty] | Summary of Available Relationships | [11 empty] | 3 | 3000 | 36.2644 | 36.2644 | 11.7477 | 11.7477 | 19.5794 | 10.9645 | 0 | 0
| Parameter | Units | Value |  | Value after Adjustment | Typical |  | [ - ] | 1 | 1 | ln V_s = ln V_0 - β*SVI - ϒ*MLSS - δ*SVI*MLSS | [11 empty] | 3.25 | 3250 | 36.237 | 36.237 | 12.7266 | 12.7266 | 18.6005 | 9.9855 | 0 | 0
| Return Rate | [ - ] | 1 |  | 1 | 0.3 - 1.2 | For conventional activated sludge plants | m/h | 0.79789 | 0.79789 |  | Daigger (SSVI_3.5) | Daigger (DSVI) | Daigger (SVI) | Ozinsky and Ekama (UCT SSVI_3.5) | Ozinsky and Ekama (Pitman SSVI_3.5) | Ozinsky and Ekama (UCT DSVI) | Ozinsky and Ekama (Pitman SVI) | Wahlberg (Stirred_1L) | Wahlberg (Unstirred_1L) | Wahlberg (Stirred_2L) | Wahlberg (Unstirred_2L) | 3.5 | 3500 | 35.9953 | 35.9953 | 13.7056 | 13.7056 | 17.6215 | 9.0065 | 0 | 0
| Hydraulic Loading Rate (Overflow Rate) | gpd/sf | 469.8191 |  | 469.8191 | 1200 |  | m/h | -0.79789 | -0.79789 | ln α (m/h) | 2.076 | 2.028 | 1.871 | 2.451 | 2.7006 | 2.3085 | 2.1437 | 3.1905 | 2.9014 | 2.681 | 2.7014 | 3.75 | 3750 | 35.5728 | 35.5728 | 14.6846 | 14.6846 | 16.6425 | 8.0276 | 0 | 0
| Hydraulic Underflow Rate | gpd/sf | 469.8191 |  | 469.8191 |  |  | kg/m2-h | 3.1916 | 2.3139 | γ (L/g) | 0.0583 | 0.103 | 0.1646 | 0.16756 | 0.22632 | 0.29721 | 0.20036 | 0.245 | 0.351 | 0.211 | 0.261 | 4 | 4000 | 34.999 | 34.999 | 15.6636 | 15.6636 | 15.6636 | 7.0486 | 0 | 0
| Clarifier Solids Loading Rate | lbs/sf-d | 15.6636 |  | 11.3561 | 35 |  |  |  |  | δ (L/mL) | 0.00405 | 0.002555 | 0.001586 | 0.00218 | 0.00264 | 0.00095 | 0.00091 | 0.00296 | 0.00058 | 0.00236 | 0.00166 | 4.25 | 4250 | 34.2999 | 34.2999 | 16.6425 | 16.6425 | 14.6846 | 6.0696 | 0 | 0
| RAS TSS Concentration | mg/L | 8000 |  | 5800 | [5 empty] | β (g/mL) | 0 | 0 | 0 | 0.00636 | 0.00808 | 0.00297 | 0.00165 | 0.01073 | 0.00602 | 0.00593 | 0.0037 | 4.5 | 4500 | 33.4985 | 33.4985 | 17.6215 | 17.6215 | 13.7056 | 5.0907 | 0 | 0
[23 empty] | 4.75 | 4750 | 32.6149 | 32.6149 | 18.6005 | 18.6005 | 12.7266 | 4.1117 | 0 | 0
3 | State Point Analysis Graph | [21 empty] | 5 | 5000 | 31.6666 | 31.6666 | 19.5794 | 19.5794 | 11.7477 | 3.1327 | 0 | 0
[23 empty] | 5.25 | 5250 | 30.669 | 30.669 | 20.5584 | 20.5584 | 10.7687 | 2.1537 | 0 | 0
[11 empty] | Applied Settleability Curve | #1 | #2 | [9 empty] | 5.5 | 5500 | 29.6355 | 29.6355 | 21.5374 | 21.5374 | 9.7897 | 1.1748 | 0 | 0
[11 empty] | Curve Applied | Daigger (SVI) | Daigger (SVI) | [9 empty] | 5.75 | 5750 | 28.5776 | 28.5776 | 22.5164 | 22.5164 | 8.8107 | 0.19579 | 0 | 0
[12 empty] | 3 | 3 | [9 empty] | 6 | 6000 | 27.5054 | 27.5054 | 23.4953 | 23.4953 | 7.8318 | -0.78318 | 0 | 0
[11 empty] | ln α | 1.871 | 1.871 | [9 empty] | 6.25 | 6250 | 26.4275 | 26.4275 | 24.4743 | 24.4743 | 6.8528 | -1.7621 | 0 | 0
[11 empty] | γ | 0.1646 | 0.1646 | [9 empty] | 6.5 | 6500 | 25.3512 | 25.3512 | 25.4533 | 25.4533 | 5.8738 | -2.7411 | 0 | 0
[11 empty] | δ | 0.001586 | 0.001586 | [9 empty] | 6.75 | 6750 | 24.2828 | 24.2828 | 26.4322 | 26.4322 | 4.8949 | -3.7201 | 0 | 0
[11 empty] | β | 0 | 0 | [9 empty] | 7 | 7000 | 23.2274 | 23.2274 | 27.4112 | 27.4112 | 3.9159 | -4.6991 | 0 | 0
[23 empty] | 7.25 | 7250 | 22.1896 | 22.1896 | 28.3902 | 28.3902 | 2.9369 | -5.678 | 0 | 0
[12 empty] | 6.4948 | 6.4948 | [9 empty] | 7.5 | 7500 | 21.173 | 21.173 | 29.3692 | 29.3692 | 1.9579 | -6.657 | 0 | 0
[23 empty] | 7.75 | 7750 | 20.1805 | 20.1805 | 30.3481 | 30.3481 | 0.97897 | -7.636 | 0 | 0
[23 empty] | 8 | 8000 | 19.2145 | 19.2145 | 31.3271 | 31.3271 | 0 | -8.615 | 0 | 0
[23 empty] | 8.25 | 8250 | 18.2769 | 18.2769 | 32.3061 | 32.3061 | -0.97897 | -9.5939 | 0 | 0
[23 empty] | 8.5 | 8500 | 17.3691 | 17.3691 | 33.285 | 33.285 | -1.9579 | -10.5729 | 0 | 0
[23 empty] | 8.75 | 8750 | 16.492 | 16.492 | 34.264 | 34.264 | -2.9369 | -11.5519 | 0 | 0
[11 empty] | Overloading Search | #1 | #2 | [9 empty] | 9 | 9000 | 15.6465 | 15.6465 | 35.243 | 35.243 | -3.9159 | -12.5308 | 0 | 0
[11 empty] | MLSS | 4000 | 2900 | [9 empty] | 9.25 | 9250 | 14.8329 | 14.8329 | 36.222 | 36.222 | -4.8949 | -13.5098 | 0 | 0
[11 empty] | Loading | 15.6636 | 11.3561 | [9 empty] | 9.5 | 9500 | 14.0513 | 14.0513 | 37.2009 | 37.2009 | -5.8738 | -14.4888 | 0 | 0
[11 empty] | Row Lookup | 16 | 11 | [9 empty] | 9.75 | 9750 | 13.3017 | 13.3017 | 38.1799 | 38.1799 | -6.8528 | -15.4678 | 0 | 0
4 | Interpretation and Adjustments | [9 empty] | Flux Below MLSS | 35.5728 | 35.5207 | [9 empty] | 10 | 10000 | 12.5838 | 12.5838 | 39.1589 | 39.1589 | -7.8318 | -16.4467 | 0 | 0
|  |  | Before Adjustments |  | After Adjustments | [5 empty] | Flux Above MLSS | 34.999 | 36.0398 | [9 empty] | 10.25 | 10250 | 11.8972 | 11.8972 | 40.1378 | 40.1378 | -8.8107 | -17.4257 | 0 | 0
a | Potential Thickening Failure? |  | No |  | No | [5 empty] | Hydraulically Overloaded? (1=yes) | 0 | 0 | [9 empty] | 10.5 | 10500 | 11.2414 | 11.2414 | 41.1168 | 41.1168 | -9.7897 | -18.4047 | 0 | 0
| If Yes, adjustments may include: | • Increase RAS flow | [20 empty] | 10.75 | 10750 | 10.6157 | 10.6157 | 42.0958 | 42.0958 | -10.7687 | -19.3836 | 0 | 0
|  | • Consider changes in 4b that may help if RAS flow adjustment is not reasonable | [8 empty] | Conversion Factors | [11 empty] | 11 | 11000 | 10.0194 | 10.0194 | 43.0748 | 43.0748 | -11.7477 | -20.3626 | 0 | 0
|  | • Consider changes in 4d if poorly settling solids are the primary cause | [8 empty] | 4.9078 | lbs/sf-d | in 1 kg/m2-h | [9 empty] | 11.25 | 11250 | 9.4517 | 9.4517 | 44.0537 | 44.0537 | -12.7266 | -21.3416 | 0 | 0
[11 empty] | 588.8256 | gpd/sf | in 1 m/h | [9 empty] | 11.5 | 11500 | 8.9118 | 8.9118 | 45.0327 | 45.0327 | -13.7056 | -22.3206 | 0 | 0
b | Overloaded? |  | No |  | No | [5 empty] | 3788.5836 | MG | in 1 m3 | [9 empty] | 11.75 | 11750 | 8.3987 | 8.3987 | 46.0117 | 46.0117 | -14.6846 | -23.2995 | 0 | 0
| If Yes, adjustments may include: | • Decrease MLSS by increasing WAS flow (decrease SRT). | [20 empty] | 12 | 12000 | 7.9116 | 7.9116 | 46.9907 | 46.9907 | -15.6636 | -24.2785 | 0 | 0
|  | • If available, convert process to step-feed and contact stabilization mode. | [20 empty] | 12.25 | 12250 | 7.4495 | 7.4495 | 47.9696 | 47.9696 | -16.6425 | -25.2575 | 0 | 0
|  | • Bring offline clarifiers online | [20 empty] | 12.5 | 12500 | 7.0115 | 7.0115 | 48.9486 | 48.9486 | -17.6215 | -26.2364 | 0 | 0
|  | • Consider changes in 4d if poorly settling solids are the primary cause | [20 empty] | 12.75 | 12750 | 6.5966 | 6.5966 | 49.9276 | 49.9276 | -18.6005 | -27.2154 | 0 | 0
[23 empty] | 13 | 13000 | 6.2039 | 6.2039 | 50.9065 | 50.9065 | -19.5794 | -28.1944 | 0 | 0
c | Underloaded without Thickening Failure? |  | Yes |  | Yes | [17 empty] | 13.25 | 13250 | 5.8324 | 5.8324 | 51.8855 | 51.8855 | -20.5584 | -29.1734 | 0 | 0
| If Yes, consider the following optimization | • Decrease RAS flow | [20 empty] | 13.5 | 13500 | 5.4811 | 5.4811 | 52.8645 | 52.8645 | -21.5374 | -30.1523 | 0 | 0
| If No, consider adjustments shown in 4a & 4b | [21 empty] | 13.75 | 13750 | 5.1493 | 5.1493 | 53.8435 | 53.8435 | -22.5164 | -31.1313 | 0 | 0
[23 empty] | 14 | 14000 | 4.836 | 4.836 | 54.8224 | 54.8224 | -23.4953 | -32.1103 | 0 | 0
d | Poor settleability Based on SVI? |  | No |  | No | [17 empty] | 14.5 | 14500 | 4.2613 | 4.2613 | 56.7804 | 56.7804 | -25.4533 | -34.0682 | 0 | 0
| SVI of poorly settling solids = | 150 | (this value will be very site dependent and must be determined by operators) | [19 empty] | 15 | 15000 | 3.7504 | 3.7504 | 58.7383 | 58.7383 | -27.4112 | -36.0262 | 0 | 0
| If Yes, adjustments may include: | • Chlorinating RAS (2-8 lbs/d per 1000 lbs MLSS) | [20 empty] | 15.5 | 15500 | 3.2972 | 3.2972 | 60.6963 | 60.6963 | -29.3692 | -37.9841 | 0 | 0
|  | • If filamentous solids are the problem, consider increasing wasting rate to waste-out the nuissance organisms. Do not increase wasting more than 10% per day or such that SRT decreases below minimum required for nitrification. | [20 empty] | 16 | 16000 | 2.8957 | 2.8957 | 62.6542 | 62.6542 | -31.3271 | -39.9421 | 0 | 0
|  | • If DO levels are < 0.5 mg/L throughout the basin, consider increasing DO | [20 empty] | 16.5 | 16500 | 2.5406 | 2.5406 | 64.6121 | 64.6121 | -33.285 | -41.9 | 0 | 0
|  | • Coordinate with Pretreatment program if source of poorly settling solids could be an industrial discharge | [20 empty] | 17 | 17000 | 2.227 | 2.227 | 66.5701 | 66.5701 | -35.243 | -43.8579 | 0 | 0
|  | • If systemic, consider major process changes to incorporate selector zones, ballast (magnetite) or surface wasting | [20 empty] | 17.5 | 17500 | 1.9504 | 1.9504 | 68.528 | 68.528 | -37.2009 | -45.8159 | 0 | 0
[23 empty] | 18 | 18000 | 1.7068 | 1.7068 | 70.486 | 70.486 | -39.1589 | -47.7738 | 0 | 0
5 | Estimate of MLSS after SRT or WAS adjustment | [21 empty] | 18.5 | 18500 | 1.4924 | 1.4924 | 72.4439 | 72.4439 | -41.1168 | -49.7318 | 0 | 0
| Parameter | Units | Current Measurements |  | Value after Adjustment | [17 empty] | 19 | 19000 | 1.304 | 1.304 | 74.4019 | 74.4019 | -43.0748 | -51.6897 | 0 | 0
| Target SRT | d | 10 |  | 9 | [17 empty] | 19.5 | 19500 | 1.1386 | 1.1386 | 76.3598 | 76.3598 | -45.0327 | -53.6477 | 0 | 0
| 7-day Average Influent Flow | MGD | 2.6 |  | 2.6 | [17 empty] | 20 | 20000 | 0.99358 | 0.99358 | 78.3178 | 78.3178 | -46.9907 | -55.6056 | 0 | 0
| 7-day Average Influent BOD Concentration | mg/L | 150 |  | 150 | [23 empty] | 33 | 24 | 0 | 0
| Temperature | °C | 25 |  | 25
| Estimated MLSS | mg/L | 3271.0208 |  | 2993.1673 | MLSS value in Section (1) needs to match this value for wasting rate to be accurate
| Estimated Daily Wasting Rate | gpd | 31987.5742 |  | 45180.1145
| Percent Change in Wasting Rate | % | N/A |  | 41.24% | (Wasting rate should not change more than 10% per day)
| BOD | lbs/d | 3252.6 |  | 3252.6
| COD | lbs/d | 6505.2 |  | 6505.2
| bCOD | lbs/d | 5074.056 |  | 5074.056
| Unbiodegradable Particulate | lbs/d | 659.3108 |  | 659.3108
| Inorganic Suspended Solids | lbs/d | 1036.4952 |  | 1036.4952
| VSS Production | lbs | 16006.5821 |  | 14751.8044 |  | L_bCOD*((Y_Hv*SRT)/(1+b_H_T*SRT))*(1+f_H*b_H_T*SRT)+L_ubpCOD*SRT
| Fraction of active OHO in MLSS | [-] | 0.3785 |  | 0.39894 |  | 1/(1+f_H*b_H_T*SRT+(f_s_up/(f_cv*Y_Hv*(1-f_s_up-f_s_us)))*(1+b_H_T*SRT))
| Inert Solids Load | lbs | 11273.7314 |  | 10211.2109 |  | L_ISS*SRT+f_iOHO*f_OHO*VSS Prod
| TSS Production | lbs | 27280.3136 |  | 24963.0152
f_s_up | Fraction of unbiodegradable particulate COD | g-CODnbp / g-CODt | 0.15
f_s_us | Fraction of unbiodegradable soluble COD | g-CODnbs / g-CODt | 0.07
f_cv | COD in VSS | g-CODx / g-VSS | 1.48
Y_Hv | Yield for OHO | g-VSS / g-CODs | 0.45
f_H | Endogenous residue fraction |  | 0.2
f_n | Fraction of undegradable N in VSS |  | 0.1
b_H_20 | Endogenous respiration rate | 1/d | 0.24
theta_b_H | Temperature adjustment for ER |  | 1.029
f_iOHO | Fraction of ISS in OHO |  | 0.15

## About
Revision | 2.1
Date | 2019-12-05
About | Developed to provide operators a simple method for assessing different secondary clarifier operational changes
If used as an operational tool, this spreadsheet will help get operators in the ballpark of good operation.
The spreadsheet is not authoritative and does not replace operator experience and know-how.
For Questions and Suggestions, Contact:
Nick Landes, Ph.D., P.E.
Freese and Nichols, Inc.
| email | nick.landes@freese.com
| mobile | 817-937-9185
| office | 817-735-7571